## SETTING
## SETTING: các cài đặt tính toán ## for comment
## GENERAL | VALUE
GE_PowerUnit | kw
GE_Sbase | 10000
GE_ZSwitch | 1e-5
## POWERFLOW
PF_Algo | PSM
PF_option_PSM | 200 | 1e-08
PF_option_GS | 200 | 1e-5
PF_option_NR | 200 | 1e-5
## BRANCHING
BR_RateMaxLine[%] | 100 | 1e3
BR_RateMaxTRF[%] | 100 | 1e3
BR_Umax[pu] | 1.1 | 1e4
BR_Umin[pu] | 0.9 | 1e4
BR_cosPhiP | 0.85 | 1e4
BR_cosPhiN | 0.95 | 1e4
## RECLOSEROPTIMISATION: K_number and K_power, default=1
RO_Recloser_number | 1
RO_K_number | 1
RO_K_power | 1
Note on A3: Đơn vị công suất [kw,mw]
Note on A4: Sbase[kva or mva]
Note on A5: z[pu] của các đoạn dây ngắn, hoặc MC/DCL
Note on A8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PSM, GS,NR,...
Note on A9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PSM (maxIteration,Epsilon)
Note on A10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: PSM (maxIteration,Epsilon)
Note on A11: NR(maxIteration,Epsilon)
Note on A14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Value,penality
Note on A15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Value,penality
Note on A16: Giới hạn, hàm phạt về điện áp cao
Note on A17: Giới hạn, hàm phạt về điện áp thấp
Note on A18: Giới hạn, hàm phạt cosPhi nguồn (phát CSPK)
Note on A19: Giới hạn, hàm phạt cosPhi nguồn (hút CSPK)
Note on A22: Số lượng Recloser cần tối ưu
Note on A23: Trọng số xét đến số lượng phụ tải
Note on A24: Trọng số xét đến công suất phụ tải

## BUS
## BUSDATA: thông tin cơ bản về BUS và phụ tải
ID | NAME | kV | FLAG | FLAG2 | PLOAD | QLOAD | nLOAD | Load Profile | xCoord | yCoord | PLOT | MEMO
1 | BUS1 | 12 | 1 | 0 |  |  |  |  | 1 | 0 |  | đơn vị kva,kw
2 | BUS2 | 12 | 1 | 0 | 200 | 300 | 200 | p1 | 2 | 0 |  |  | 100
3 | BUS3 | 12 | 1 | 0 | 200 | 300 | 200 | p1 | 3 | 0 |  |  | 100
4 | BUS4 | 12 | 1 | 0 | 200 | 300 | 200 | p1 | 4 | 0 |  |  | 100
5 | BUS5 | 12 | 1 | 0 | 200 | 300 | 200 | p1 | 5 | 0 |  |  | 100
6 | BUS6 | 12 | 1 | 1 | 800 | 2400 | 800 | p1 | 6 | 0 |  |  | 800
7 | BUS7 | 12 | 1 | 0 | 150 | 300 | 150 | p1 | 2 | -1 |  |  | 100
8 | BUS8 | 12 | 1 | 1 | 200 | 300 | 200 | p1 | 2 | -2 |  |  | 100
9 | BUS9 | 12 | 1 | 0 | 20000 | 50000 | 0 | p1 | 4 | -1 |  |  | 0
10 | BUS10 | 12 | 1 | 0 | 20000 | 50000 | 20000 | p1 | 4 | -2 |  |  | 100
11 | BUS11 | 12 | 1 | 0 | 200 | 300 | 200 | p1 | 5 | -1 |  |  | 100
12 | BUS12 | 12 | 1 | 0 |  |  |  |  | 4 | -3
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Số nút (duy nhất)
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tên nút
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Điện áp định mức nút
Note on D2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1-Inservice; 0- Out of service
Note on E2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: Shunt có thể đóng/mở (branching)
Note on F2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Công suất tác dụng của phụ tải
Note on G2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Công suất phản kháng của phụ tải
Note on H2: Số lượng phụ tải, sử dụng cho bài toán tối ưu vị trí đặt Recloser
Note on I2: Biểu đồ phụ tải bỏ trống: nếu fixed p1,p2… theo biểu đồ số p1,p2 biểu đồ theo [pu]
Note on J2: tọa độ x plot
Note on K2: tọa độ y plot
Note on L2: plot kết quả tính toán; 1,2,5 1: tên bus 2: điện áp định mức bus 3: ID bus 4: điện áp bus [pu] 5: điện áp bus [kv]
Note on M2: Các ghi chú

## SOURCE
## SOURCEDATA: thông tin về nguồn
ID | BUS_ID | NAME | kV | FLAG | CODE | vGen [pu] | aGen [deg] | Pgen | Qmax | Qmin | vGen Profile | pGen Profile | PLOT | MEMO
1 | 1 | BUS1 | 12 | 1 | 3 | 1 | 0 |  | 99999 | -99999 | p2 |  |  | đơn vị kva,kw
2 | 12 | BUS12 | 12 | 1 | 2 | 1 | 0 | 500 | 99999 | -99999 | p2
`
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Số nút (duy nhất)
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tên nút
Note on D2: kV nút được VLOOPUP từ sheet BUS
Note on E2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1-Inservice; 0- Out of service
Note on F2: 3: feeder or Swing BUS 2: Generator of PV BUS
Note on G2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Điện áp đặt tại cho Bus nguồn >0
Note on H2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Điện áp đặt tại cho Bus nguồn >0
Note on I2: công suất phát nguồn, nếu slack bus thì để trống hoặc =0)
Note on J2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Công suất Q cực đại (của Bus nguồn)
Note on K2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Công suất Q cực đại (của Bus nguồn)
Note on L2: Biểu đồ điện áp nguồn
Note on M2: Biểu đồ công suất phát của nguồn
Note on N2: plot kết quả tính toán; 1,2,5 1: pn[kw] 10: pn[mw] 2: pgen[kw] 20: pgen[mw] 3: qgen[kw] 30: qgen[mw]
Note on O2: Các ghi chú

## SHUNT
## SHUNTDATA: thông tin về tụ/ kháng bù ngang
ID | BUS_ID | NAME | kV | Qshunt | deltaP | FLAG | FLAG3 | shunt Profile | PLOT | MEMO
1 | 4 | BUS4 | 12 | 500 | 0 | 0 | 1 |  |  | đơn vị kva,kw
2 | 9 | BUS9 | 12 | 200 | 0 | 0 | 1
3 | 9 | BUS9 | 12 | 200 | 0 | 0 | 1
4 | 10 | BUS10 | 12 | 50 | 0 | 0 | 1
Note on B2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Số nút (duy nhất)
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tên nút
Note on D2: kV nút được VLOOPUP từ sheet BUS
Note on E2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: >0: capacitive; <0 reactive
Note on F2: Tổn thất cs tác dụng [kw] tại điện áp định mức (của lưới)
Note on G2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1-Inservice; 0- Out of service
Note on H2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: Shunt có thể đóng/mở (branching)
Note on I2: Biểu đồ công suất phát của nguồn
Note on J2: plot kết quả tính toán; 1,10 1: q [kva] 10: q[mva]
Note on K2: Các ghi chú

## LINE
## LINEDATA
ID | BUS_ID1 | BUS_ID2 | NAME BUS | kV | CID | FLAG | FLAG2 | FLAG3 | LENGTH [km] | nFault [per km per year] | R [Ohm/km] | X [Ohm/km] | B [microS/km] | RATEA [A] | xCoord | yCoord | PLOT | MEMO
1 | 2 | 1 | BUS2-BUS1 | 12 | 1 | 1 | 0 | 0 | 3 | 1 | 0.21 | 0.41 | 0 | 300
2 | 3 | 2 | BUS3-BUS2 | 12 | 1 | 1 | 1 | 1 | 3.5 | 1 | 0.21 | 0.41 | 0 | 200
3 | 4 | 3 | BUS4-BUS3 | 12 | 1 | 1 | 1 | 1 | 3 | 1 | 0.21 | 0.41 | 0 | 300
4 | 4 | 5 | BUS4-BUS5 | 12 | 1 | 1 | 1 | 1 | 3.5 | 1 | 0.21 | 0.41 | 700 | 300
5 | 6 | 5 | BUS6-BUS5 | 12 | 1 | 1 | 1 | 1 | 2.5 | 1 | 0.21 | 0.41 | 0 | 300
6 | 2 | 7 | BUS2-BUS7 | 12 | 1 | 1 | 1 | 1 | 3 | 1 | 0.21 | 0.41 | 0 | 300
7 | 7 | 8 | BUS7-BUS8 | 12 | 1 | 1 | 1 | 1 | 3.5 | 1 | 0.21 | 0.41 | 0 | 300
8 | 9 | 4 | BUS9-BUS4 | 12 | 1 | 1 | 1 | 1 | 2.5 | 1 | 0.21 | 0.41 | 500 | 300
9 | 10 | 9 | BUS10-BUS9 | 12 | 1 | 1 | 1 | 1 | 2.5 | 1 | 0.21 | 0.41 | 0 | 300
10 | 12 | 10 | BUS12-BUS10 | 12 | 1 | 1 | 1 | 1 | 3.5 | 1 | 0.21 | 0.41 | 0 | 300
11 | 11 | 5 | BUS11-BUS5 | 12 | 1 | 1 | 1 | 1 | 3.5 | 1 | 0.21 | 0.41 | 0 | 300
12 | 7 | 9 | BUS7-BUS9 | 12 | 1 | 1 | 1 | 1 | 3.5 | 1 | 0.21 | 0.41 | 0 | 300
13 | 9 | 11 | BUS9-BUS11 | 12 | 1 | 0 | 1 | 1 | 3.5 | 1 | 0.21 | 0.41 | 0 | 300
14 | 8 | 10 | BUS8-BUS10 | 12 | 1 | 0 | 1 | 1 | 3.5 | 1 | 0.21 | 0.41 | 0 | 300
15 | 11 | 12 | BUS11-BUS12 | 12 | 1 | 0 | 1 | 1 | 3.5 | 1 | 0.21 | 0.41 | 0 | 300 | 5 | -3
16 | 10 | 11 | BUS10-BUS11 | 12 | 1 | 0 | 1 | 1 | 3.5 | 1 | 0.21 | 0.41 | 0 | 300
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Số thứ tự Line, duy nhất >1000
Note on B2: Số nút Bus đầu
Note on C2: Số nút Bus cuối
Note on D2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tên nút
Note on E2: kV nút được VLOOPUP từ sheet BUS
Note on F2: Circuit ID
Note on G2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1-Inservice; 0- Out of service; dùng để lưu trữ dự liệu thô
Note on H2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: có thể đóng/mở (branching)
Note on I2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1: có thể đóng/mở (branching)
Note on J2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Length of Line (km)
Note on K2: Số lần sự cố /km /năm (bài toán tối ưu vị trí đặt Recloser)
Note on O2: Dòng định mức
Note on P2: tọa độ x plot cho các điểm rẽ
Note on Q2: tọa độ y plot cho các điểm rẽ
Note on R2: Plot kết quả đầu ra: 1: pq[kw] đầu 1 2: pq[kw] đầu 2 11: pq[mw] đầu 1 12: pq[mw] đầu 2 31: i[a] đầu 1 32: i[a] đầu 2 100: rate%
Note on S2: Các ghi chú

## TRF2
## MBA2DATA: dữ liệu máy biến áp 2 cuộn dây
ID | BUS_ID1 | BUS_ID2 | NAME BUS | kV | CID | NAME MBA2 | FLAG | Sn | uk [%] | pk | P0 | i0 [%] | PLOT | MEMO
1 | 1 | 2 | BUS1-BUS2 | 12 | 1 | T1 | 0 | 400 | 10 | 12 | 3 | 0.3
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Số thứ tự Line, duy nhất >1000
Note on B2: Số nút Bus đầu
Note on C2: Số nút Bus cuối
Note on D2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tên nút
Note on E2: kV nút được VLOOPUP từ sheet BUS
Note on F2: Circuit ID
Note on H2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1-Inservice; 0- Out of service; dùng để lưu trữ dự liệu thô
Note on I2: Công suất định mức [kva]
Note on J2: Điện áp ngắn mạch %
Note on K2: Tổn thất ngắn mạch
Note on L2: Tổn thất không tải
Note on M2: Dòng không tải
Note on N2: Plot kết quả đầu ra: 1: pq[kw] đầu 1 2: pq[kw] đầu 2 11: pq[mw] đầu 1 12: pq[mw] đầu 2 31: i[a] đầu 1 32: i[a] đầu 2 100: rate max (1,2) 101: rate% cuộn 1 102: rate% cuộn 2
Note on O2: Các ghi chú

## TRF3
## MBA3DATA: dữ liệu máy biến áp 3 cuộn dây
ID | BUS_ID1 | BUS_ID2 | BUS_ID3 | NAME BUS | CID | NAME MBA3 | FLAG | Sn1 | Sn2 | Sn3 | uk1-2 [%] | uk1-3 [%] | uk2-3 [%] | pk1-2 | pk1-3 | pk2-3 | P0 | i0 [%] | PLOT | MEMO
1 | 8 | 10 | 12 | BUS8-BUS10-BUS12 | 1 | AT1 | 0 | 25000 | 25000 | 10000 | 12 | 25 | 18 | 15 | 16 | 12 | 18 | 0.03 |  | đơn vị kw
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Số thứ tự Line, duy nhất >1000
Note on B2: Số nút Bus đầu
Note on C2: Số nút Bus 2
Note on D2: Số nút Bus 3
Note on E2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tên nút
Note on F2: Circuit ID
Note on H2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1-Inservice; 0- Out of service; dùng để lưu trữ dự liệu thô
Note on I2: Công suất định mức cuộn 1 [kva]
Note on J2: Công suất định mức cuộn 2 [kva]
Note on K2: Công suất định mức cuộn 2 [kva]
Note on L2: Điện áp ngắn mạch 1-2 %
Note on M2: Điện áp ngắn mạch 1-3 %
Note on N2: Điện áp ngắn mạch 2-3 %
Note on O2: tổn thất ngắn mạch 1-2 kw
Note on P2: tổn thất ngắn mạch 1-3 kw
Note on Q2: tổn thất ngắn mạch 2-3 kw
Note on R2: Tổn thất không tải
Note on S2: Dòng không tải
Note on T2: Plot kết quả đầu ra: 1: pq[kw] đầu 1 2: pq[kw] đầu 2 2: pq[kw] đầu 3 11: pq[mw] đầu 1 12: pq[mw] đầu 2 13: pq[mw] đầu 3 31: i[a] đầu 1 32: i[a] đầu 2 33: i[a] đầu 3 100: rate max (1,2,3) 101: rate% cuộn 1 102: rate% cuộn 2 103: rate% cuộn 3
Note on U2: Các ghi chú

## PROFILE
## PROFILE_DATA
ID | deltaTime | MEMO | p1 | p2
1 | 1 |  | 1 | 1
2 | 1 |  | 1 | 1
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Số nút của tải
Note on B2: Thời gian cho mỗi điểm của profile, 0.25: 15 phút 0.5: 30 phút 1: 1h
Note on D2: tên profile

## SHUNT_PLACEMENT
## QSHUNT_DATA: số liệu các bộ tụ (dùng cho bài toán tối ưu đặt tụ)
ID | kV | Qshunt | Number | deltaP | FLAG | MEMO
1 | 12 | 500 | 5 | 0 | 1 | đơn vị kva,kw
2 | 12 | 200 | 3 | 0 | 1
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Số nút của tải
Note on B2: điện áp định mức [kV]
Note on C2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: >0: capacitive; <0 reactive
Note on D2: Số lượng bộ tụ
Note on E2: Tổn thất [kW] mỗi bộ ở điện áp định mức
Note on F2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 1-Inservice; 0- Out of service
Note on G2: Các ghi chú

## PROFILE2
## PROFILE_DATA
ID | deltaTime | MEMO | p1 | p2
1 | 1 |  | 1.01 | 1.02
2 | 1 |  | 0.65 | 1.05
3 | 1 |  | 0.6 | 1.03
4 | 1 |  | 0.5 | 1.04
5 | 1 |  | 0.52 | 1.03
6 | 1 |  | 0.6 | 1.03
7 | 1 |  | 0.8 | 1.02
8 | 1 |  | 0.85 | 1.01
9 | 1 |  | 0.86 | 1.01
10 | 1 |  | 0.88 | 1
11 | 1 |  | 0.9 | 1
12 | 1 |  | 0.92 | 1
13 | 1 |  | 0.94 | 1
14 | 1 |  | 0.96 | 1
15 | 1 |  | 1 | 1
16 | 1 |  | 0.96 | 1
17 | 1 |  | 0.94 | 1
18 | 1 |  | 0.9 | 1
19 | 1 |  | 0.85 | 1.01
20 | 1 |  | 0.9 | 1.01
21 | 1 |  | 0.85 | 1.01
22 | 1 |  | 0.84 | 1.01
23 | 1 |  | 0.8 | 1.02
24 | 1 |  | 0.76 | 1.02
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Số nút của tải
Note on B2: Thời gian cho mỗi điểm của profile, 0.25: 15 phút 0.5: 30 phút 1: 1h
Note on D2: tên profile